## Resistivity Data
TABLE 1 Apparent Resistivity Data
Client: |  | Penn E&R | [5 empty] | Date: |  | 2023-09-21
Project Name: |  | B50123 LAUS-SAKR Fiber and Reclosers | [5 empty] | Weather: |  | Sunny to Overcast |  | DATA INPUT TABLE
Project Location: |  | Lancaster County, Pennsylvania | [5 empty] | Temperature: |  | 74 deg. F |  | Enter measured resistance (Ω)
Equipment: |  | Allied Associates Ohmega | [9 empty] | Converts to Apparent Resistivity (Ω-ft) Below
Test Method: |  | Wenner 4 Electrode Array | [9 empty] | Converts to Apparent Resistivity (Ω-m) Left
Array |  | Array spacing (ft) | [9 empty] | Array |  | Array spacing (ft)
|  | 10 |  | 20 |  | 40 |  | 80 |  | 160 |  |  |  | 10 |  | 20 |  | 40 |  | 80 |  | 160
|  | Resistance (Ω) | Apparent Resistivity (Ω-m) | Resistance (Ω) | Apparent Resistivity (Ω-m) | Resistance (Ω) | Apparent Resistivity (Ω-m) | Resistance (Ω) | Apparent Resistivity (Ω-m) | Resistance (Ω) | Apparent Resistivity (Ω-m) |  |  | Resistance (Ω) | Apparent Resistivity (Ω-ft) | Resistance (Ω) | Apparent Resistivity (Ω-ft) | Resistance (Ω) | Apparent Resistivity (Ω-ft) | Resistance (Ω) | Apparent Resistivity (Ω-ft) | Resistance (Ω) | Apparent Resistivity (Ω-ft)
34 | Dir. 1 | 7.59 | 145.3571 | 3.356 | 128.5424 | 1.695 | 129.8447 | 1.383 | 211.8881 | 0.8628 | 264.3776 | 34 | Dir. 1 | 7.59 | 476.8934 | 3.356 | 421.727 | 1.695 | 425.9996 | 1.383 | 695.171 | 0.8628 | 867.3804
| Dir. 2 | 7.55 | 144.5911 | 3.445 | 131.9513 | 1.891 | 144.8592 | 1.321 | 202.3892 | 0.912 | 279.4533 |  | Dir. 2 | 7.55 | 474.3801 | 3.445 | 432.9111 | 1.891 | 475.2597 | 1.321 | 664.0065 | 0.912 | 916.8416
150 | Dir. 1 | 9.48 | 181.5527 | 5.919 | 226.7111 | 4.141 | 317.2194 | 2.889 | 442.621 | 1.119 | 342.8819 | 150 | Dir. 1 | 9.48 | 595.6455 | 5.919 | 743.8028 | 4.141 | 1040.7459 | 2.889 | 1452.1686 | 1.119 | 1124.9405
| Dir. 2 | 9.291 | 177.9332 | 6.025 | 230.7711 | 4.098 | 313.9254 | 3.001 | 459.7804 |  |  |  | Dir. 2 | 9.291 | 583.7703 | 6.025 | 757.1232 | 4.098 | 1029.9389 | 3.001 | 1508.4659 |  | 0
228 | Dir. 1 | 5.932 | 113.6045 | 4.334 | 166.002 | 3.296 | 252.4885 | 1.912 | 292.9357 | 1.336 | 409.3746 | 228 | Dir. 1 | 5.932 | 372.7182 | 4.334 | 544.626 | 3.296 | 828.3745 | 1.912 | 961.0752 | 1.336 | 1343.0926
| Dir. 2 | 6.002 | 114.9451 | 4.398 | 168.4534 | 3.424 | 262.2939 | 1.819 | 278.6873 | 1.384 | 424.0827 |  | Dir. 2 | 6.002 | 377.1165 | 4.398 | 552.6685 | 3.424 | 860.5443 | 1.819 | 914.3284 | 1.384 | 1391.3474
|  | Resistance (Ω) | Apparent Resistivity (Ω-m) | Resistance (Ω) | Apparent Resistivity (Ω-m) | Resistance (Ω) | Apparent Resistivity (Ω-m) | Resistance (Ω) | Apparent Resistivity (Ω-m) | Resistance (Ω) | Apparent Resistivity (Ω-m)
SITE AVG: |  | 7.6408 | 146.3306 | 4.5795 | 175.4052 | 3.0908 | 236.7718 | 2.0542 | 314.7169 | 1.1228 | 344.034